Everything you need to know about Flammable Liquids Cabinets

What is a Flammable Storage Cabinet? It is a listed cabinet designed in accordance with NFPA 30. The cabinet is designed and constructed to limit the internal temperature to no more than 325°F when subjected to a 10-minute external fire. In order to protect the contents from a fire outside the cabinet the doors MUST be kept closed & latched.

When do I need a Flammable Liquids cabinet?  You may store a maximum of 180 gallons of flammable and combustible liquids with a flash point of < 140F in a single fire area (room with one-hour fire rated walls and self-closing 20-minute fire rated doors).  Do not store ignition sources, or boxes inside a cabinet.  This amount of liquids must be stored as follows:

- Not more than 10 gallons located outside a flammable storage cabinet.

- Not more than 60 gallons in a flammable storage cabinet.

- Not more than 3 flammable storage cabinets per fire area.

In addition to the 180 gallons above, a maximum of 60 gallons of combustible liquids with a flash point  140F and <200F can be stored outside of a flammable liquids cabinet.

Flammable Liquid Storage Cabinets specifications

- Minimum wall thickness of 0.044 inches (18 gauge) metal

- Double wall construction with a minimum air gap of 1-1/2“ between walls including door, top, bottom, & sides.

- Tight-fitting joints welded or riveted.

- Liquid-tight bottom with a door sill of at least 2“.

- Three-point latch on doors. (self-closing doors recommended)

Is the cabinet required to be electrically grounded? (Recommended if dispensing from within)

NFPA 30 does not require that the cabinet itself be grounded. Many manufacturers provide a grounding screw as a convenience to the user. The user can connect this screw to a building ground & use the cabinet-mounted ground as needed to ground individual containers from which liquids are dispensed.

Labeling of cabinets: Flammable Liquid Cabinets shall be conspicuously labeled in RED letters on contrasting background; "FLAMMABLE - KEEP FIRE AWAY."

Don’t Vent Unless You Have To: NFPA 30 does not require exhaust ventilation for storage cabinets, although most cabinets have plugged fittings that can be used. Exhaust ventilation should only be provided when warranted by the stored materials, for example for particularly toxic or noxious materials. A vented cabinet could compromise the ability of the cabinet to protect its contents from a fire.

If vented, cabinet should be vented from the bottom with make-up air supplied to the top. It should be vented outdoors or through a flame arrester to an exhaust system. Construction of the venting duct should be equal to the fire rating of the cabinet.